## gen
Bus # | 1
Gen id | 1
type | GENROU
T'd0 | 6
T''d0 | 0.5
T'q0 | 1
T''q0 | 0.05
H | 2.41
D | 0
Xd | 1.4
Xq | 1.35
X'd | 0.3
X'q | 0.6
X''d=X''q | 0.2
Xl | 0.1
S(1.0) | 0
S(1.2) | 0
Ra | 0.005

## exc
Bus # | 1
Gen id | 1
type | EXDC1
Tr | 0.02
Ta | 0.02
Tc | 1
Tb | 1
Te | 0.83
Tf1 | 1.246
Kf1 | 0.0754
Ka | 10
Ke | 1

## gov
Bus # | 1
Gen id | 1
type | TGOV1
R | 0.05
T1(>0)(sec) | 0.9
V MAX | 1
V MIN | 0
T2(sec) | 1
T3(>0)(sec) | 2
Dt | 0

## gfm ibr generic
Bus # | 4
type | GFM_GENERIC
comments | Parameters from "Open-Source PSCAD Grid-Following and Grid-Forming Inverters and a Benchmark for Zero-Inertia Power System Simulations", Kenyon et al. (NREL).
MVA base | 200
Base kV | 16.5
Lf | 0.15
Rf | 0.005
Cf (uF) | 2.5
Rcap | 0.005
Lc | 0.15
Rc | 0.005
kC_i | 1.19
kC_p | 0.73
GC | 1
kV_i | 1.16
kV_p | 0.52
GV | 1
wmeas | 120
droopPercentP | 0.05
droopPercentQ | 0.05
w_VR | 30
Rv | 0.2

## zip load
Bus # | 2 | 3
type | ZIP | ZIP
comments | P split from "Implementation of the WECC Composite Load Model for Utilities using the Component-Based Modeling Approach" (normalised within the ZIP category). Q taken as pure impedance per NERC "Reliability Guideline: Developing Load Model Composition Data" (2017). Tau is the Simscape default ZIP filter time constant. | P split from "Implementation of the WECC Composite Load Model for Utilities using the Component-Based Modeling Approach" (normalised within the ZIP category). Q taken as pure impedance per NERC "Reliability Guideline: Developing Load Model Composition Data" (2017). Tau is the Simscape default ZIP filter time constant.
Pz | 0.22 | 0.22
Pi | 0.33 | 0.33
Pp | 0.45 | 0.45
Qz | 1 | 1
Qi | 0 | 0
Qp | 0 | 0
Tau | 0.1 | 0.1

## im load kundur
Bus # | 2 | 3
type | IM_KUNDUR | IM_KUNDUR
comments | Small industrial motor, Kundur "Power System Stability and Control" section 7.4.3.c; values already in per unit. powerPercent (motor share of bus MW) from the WECC composite load component-based modelling paper. PF is an approximation used only to size the motor MVA base. | Small industrial motor, Kundur "Power System Stability and Control" section 7.4.3.c; values already in per unit. powerPercent (motor share of bus MW) from the WECC composite load component-based modelling paper. PF is an approximation used only to size the motor MVA base.
powerPercent | 0.55 | 0.55
Rs | 0.078 | 0.078
Rr | 0.044 | 0.044
Xm | 2.67 | 2.67
Xs | 0.065 | 0.065
Xr | 0.049 | 0.049
H | 0.5 | 0.5
m | 2 | 2
PF | 0.85 | 0.85